## Users' manual
Solar O&M Best Practices Mark Checklist (India edition 2021) - Users' Manual

## Checklist
Solar O&M Best Practices Mark Checklist (India edition 2021)
Learn more about the Solar O&M Best Practices Mark here: |  | 2021 India edition (04.03.2021) |  |  |  |  | The Solar Best Practices Mark is powered and maintained by SolarPower Europe. www.solarpowereurope.org
www.solarbestpractices.com | [6 empty] | The requirements are based on SolarPower Europe's Operation & Maintenance Best Practices Guidelines Version 4.0. Download here.
O&M Contractor details |  |  | O&M Contractor logo
Company name: | [Company name] |  | Insert your logo here |  |  |  | Maximum Score: | 100
Address: | [Address] | [5 empty] | Score needed for compliance: | 80
Website: | [Website] | [5 empty] | [Company name]'s score: | 0
Contact person: | [Contact person] | [5 empty] | [Company name]'s result:
E-Mail: | [E-Mail] | [5 empty] | [Company name] does not meet the eligibility criteria of the Solar O&M Best Practices Mark
Phone: | [Phone]
# | Requirements title and description | Max Score | Self-evaluation |  |  | Your Score | Explanations | Documents for the technical dossier | Calculation (this is not invisible to users)
A | Environment, Health & Safety (EH&S) | 15 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0 |  |  | Answer (3=fully, 2=party, 1=not fulfilled) | Value
A.1 | Detection of environmental problems and social impacts | 2 |  |  |  | 0 | The O&M Contractor detects and handles environmental problems promptly, following precise rules, described in procedures well known by the personnel. The O&M Contractor complies with the requirements of the Environmental Social Impact Assessment (ESIA) and the Environmental Social Management Plan (ESMP). | According to national legislation, where required: - Hazard Plans and Risk Evaluation Documents - Waste disposal and recycling registers - EH&S Internal Procedures and Instruction. This set of document should include for example: - Personal Protection Equipment list and rules - Visitors and subcontractors management - Personnel training and medical control - Examples of subcontractor safety documentation used to approve subcontractors' employment - Example ESIA and ESMP, for example The World Bank's Environmental and Social Framework (ESF) and Environmental, Social, Health and Safety (ESHS). | 1 | 0%
A.2 | Marking of hazardous/dangerous areas and equipment | 2 |  |  |  | 0 | Hazardous areas and equipment are appropriately marked and all the people visiting the plants are properly informed of hazards. |  | 1 | 0%
A.3 | Safety training and equipment | 3 |  |  |  | 0 | The O&M Contractor's personnel (including subcontrators, if applicable) has received appropriate safety training and has the necessary safety equipment. |  | 1 | 0%
A.4 | Compliance with local Health & Safety legislations/guidelines | 4 |  |  |  | 0 | The O&M Contractor ensures that it complies, and that all of its subcontractors comply, at all times with the relevant EH&S legislation/guidelines. |  | 1 | 0%
A.5 | Waste disposal, recycling and reuse | 2 |  |  |  | 0 | The O&M Contractor disposes of waste materials in line with international best practices and, when possible or mandatory (especially modules) recycles or reuses broken parts. |  | 1 | 0%
A.6 | EH&S management systems: OHSAS 18001 or ISO 14001 certifications | 2 |  |  |  | 0 | The O&M Contractor has in place one of the certifications. | - Copies of valid certificates | 1 | 0%
B | Personnel & training | 9 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
B.1 | Structured and appropriate company organisation | 2 |  |  |  | 0 | Based on the size of the O&M Contractor company, an appropriate managerial organisation is in place to perform the contractual activities. Mark "Fully fulfilled" only if you can provide a detailed organisation chart and key job profiles. | - Organisation chart with key job profiles and responsibilities | 1 | 0%
B.2 | Proper qualifications and skills of the personnel at all levels and training programmes | 3 |  |  |  | 0 | The personnel of the O&M Contractor (including subcontractors, if applicable) has the relevant qualifications to perform the works in a safe, responsible and accountable manner. Tick "Fully fulfilled" if you possess a certificate from any authority. | - Training plan of key personnel and relevant certifications from Skill Council for Green Jobs (SCGJ). | 1 | 0%
B.3 | Specific training and certification of Site Technicians | 4 |  |  |  | 0 | The Site Technicians of the O&M Contractor (including subcontractors, if applicable) have the updated certifications to work safely according to the appointment provided and the local regulations, for example: work at height, (Senior) Authorised Person etc. Tick "Fully fulfilled" if you possess a certificate from any authority. | - Full set of certificates as per local law and standards, such as electrical works, work at height,etc. and evidence of updated training courses | 1 | 0%
C | Operation Planning (Central Control Room) | 8 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0 |  |  | 2 | 50%
C.1 | Operation management - Remote Monitoring via Central Control Room | 2 |  |  |  | 0 | The O&M Contractor is organised with engineers and technicians in a way that it is able to (i) control plant performance using the monitoring systems installed centrally via the Central Control which comprises of monitoring & analytics at the portfolio level and Local Control Rooms; through a dedicated asset management software, as well as (ii) the capability to properly perform site visits and non-intrusive inspections to perform, maintenance and other potential issues on the managed plants (with own personnel or subcontractors, if applicable) and interfere with local energy authorities & regulatory compliance. | - Organisation chart with key job profiles and responsibilities - Control Room/Project management job description and procedures - Sample site report - Sample contract with subcontractor (if applicable) | 1 | 0%
C.2 | Reporting | 2 |  |  |  | 0 | The O&M Contractor prepares and provides regular reports with the indicators and values listed in Table 1 of the O&M Best Practices Guidelines (page 32). Tick "Fully fulfilled" if there is a (i) capability to produce intermediate reporting, for example when PR and Availability are affected by more than a certain threshold, or when an accident occurs as well as to properly report and control EH&S compliance and (ii) the use of a Computerised Maintenance Management System (CMMS) to measure various Key Performance Indicators (KPIs). The report shall properly describe the events (at least: name, complete location (i.e., CT06), duration, start, end, energy loss) so in case there is any doubt about the KPIs, these can be double-checked and/or recomputed. | - Sample report | 1 | 0%
C.3 | Regulatory compliance | 1 |  |  |  | 0 | The O&M Contractor ensures that the operation of the PV plant is in compliance with the relevant regulations. | - Examples of the documentation received and handled by the O&M Contractor on behalf of the Asset Owner. | 1 | 0%
C.4 | Warranty management | 1 |  |  |  | 0 | The O&M Contractor can act as the asset owner’s representative for any warranty claims vis-à-vis the Original equipment manufacturers (OEM) of PV plant components. | - Waranty management plan or examples of warranty claims managed (reports, emails etc.) | 1 | 0%
C.5 | Insurance claims | 1 |  |  |  | 0 | The O&M Contractor can act as the asset owner’s representative for any insurance claims vis-à-vis the insurance provider. | - Insurance management plan or examples of insurance claims managed (reports, emails, etc.) | 1 | 0%
C.6 | Contract management | 1 |  |  |  | 0 | The O&M Contractor is able to oversee various contractual parameters, responsibilities and obligations of the asset owner linked to the respective PV plant. | - Contract management plan or examples of contract management (reports, emails, etc.) | 1 | 0%
D | Operation execution (Local Control Room) | 18 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0 |  |  | 3 | 100%
D.1 | Documentation Management | 1 |  |  |  | 0 | The O&M Contractor's Documentation Management System includes versioning and history tracking of changes with timestamp and the respective user. Documents should be stored in a secure location (electronic or physical records) and only appropriate personel should have access to them. | - Written procedure or other internal manual that provides evidence of the documentation management - Written procedure regarding the access, hierarchy and functionability of the "electronic storage" / "cloud " | 1 | 0%
D.2 | Documentation Management innovations | 1 |  |  |  | 0 | The O&M Contractor is able to provide, directly or indirectly, some of the services described in section "13.1.7. Future best practices in document management systems". | - Description of document management system innovations | 1 | 0%
D.3 | Record control | 2 |  |  |  | 0 | The O&M Contractor's interventions (preventive, corrective or other) are kept on record or tickets and include at least essential details (acknowledgment, response and resolution times, time of intervention, duration and outcome) as well as information about the actual activities conducted, equipment/devices affected, pictures, spare parts used. The O&M Contractor is responsible for updating regularly, managing and controlling the documentation: (i) Define type of storage (physical or/and electronical), (ii) Ensure electronic copy of all documents, (iii) Ensure controlled access to documents, (iv) Ensure authorization for modifications (keep a logbook on name of person who modified the document, date of modification, reason for modification and further information), (v) Ensure history of the documents (versioning). Reference is the Input records examples in the O&M Best Practices Guidelines-D Annex. | - Written procedure - List of input records | 1 | 0%
D.4 | Grid Code Compliance | 3 |  |  |  | 0 | The O&M Contractor is able to meet the procedures, actions and activites required by the respective grid operator in order to comply with grid safety, power quality and operating speccifications. In a country like India, where grid code compliances vary vastly, It is the responsibility of the O&M Contractor to engage the respective load dispatch center (LDC). For the local operation, the O&M provider is responsible to operate the PV plant in accordance with the respective state grid code. | - Description of respective grid code requirements and necessary compliance measures. | 1 | 0%
D.5 | Resources for Operations | 2 |  |  |  | 0 | The O&M Contractor has sufficient resources with the proper skills for conducting Operations to ensure acceptable response times as well as be available to provide information and support to asset owners and/or asset managers. The O&M Contractor can appropriately control subcontractors (if applicable). The O&M Contractor has the necessary tools (softwares or others) to ensure that information is reliable and readily available upon request. | *- Organisation chart with key job profiles and responsbilities - Average number of managers/resources per MW and/or per PV plant and/or per client - List of tools (softwares or others) used - Sample subcontractor contract section defining the hierarchy between the O&M Contractor and the subcontractor (if applicable) | 1 | 0%
D.6 | Data analysis | 2 |  |  |  | 0 | The O&M Contractor performs data analysis on plant, portfolio and account level. Suitable analytical tools are employed for in-depth data analysis of performance on plant level and lower. KPIs should be calculated as per the contract and exclusion periods should be taken into consideration for any KPI calculation, as per each individual contract. | - Description of data analysis and KPI calculation capabilities | 1 | 0%
D.7 | Data analysis innovations | 1 |  |  |  | 0 | The O&M Contractor is already using some of the solutions described in section "13.1. Smart PV power plant monitoring and data-driven O&M". | - Description of Smart PV power plant monitoring and data-driven O&M capabilities | 1 | 0%
D.8 | Data security | 2 |  |  |  | 0 | The O&M Contractor has a detailed backup plan and ensures security of data by taking frequent backups and using encryption and secure protocols. | - Description of data security policies (password policies, encryption, protocols of communication) - Copy of backup plan, Recovery Time Objective (RTO) and Recovery Point Objective (RPO) | 1 | 0%
D.9 | Monitoring via Local Control Room | 3 |  |  |  | 0 | Monitoring is carried out remotely and at local stations.The O&M Contractor has a local Control Room or at least a monitoring team at both local and central levels, operating during daylight hours 365 days/year, with sufficient personnel, organised in shifts, able to supervise all the monitoring systems in use and to react at alarms. | *- Remote monitoring procedures for operations and description of activities, shifts, etc. - Control room description/photos, monitoring team description | 1 | 0%
D.10 | Management of change | 1 |  |  |  | 0 | The O&M Contractor implements changes in the design of the PV power plant according to a change management procedure in order to avoid uncontrolled modifications and manage the risk of changes. | - Document that defines the change management procedure | 1 | 0%
E | Maintenance | 18 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
E.1 | Scheduled maintenance: Annual Maintenance Plan | 3 |  |  |  | 0 | The O&M Contractor sends the Annual Maintenance Plan at the beginning of the maintenance period to the Client and updates it according to requirements and priorities of plant management. Reference is the Annual Maintenance Plan as shown in the O&M Best Practices Guidelines Annex. | - Sample Annual Maintenance Plan | 1 | 0%
E.2 | Monitoring the Annual Maintenance Plan | 2 |  |  |  | 0 | The O&M Contractor reports the activities of the Annual Maintenance Plan regularly to the Client and include O&M Contractor KPIs. Sites are inspected regularly. | - Sample report (inspection report) including the last maintenance activities | 1 | 0%
E.3 | Minimisation of loss | 3 |  |  |  | 0 | The O&M Contractor minimises the production losses caused by maintenance activities considering affected production capacities and irradiation. A effective way to reduce losses is via monitoring. The SCADA system shall have the ability to process high data volumes in order to anticipate failures and schedule corrective and preventive activities in advance. | - Sample report including losses due to maintenance activities | 1 | 0%
E.4 | Corrective maintenance | 3 |  |  |  | 0 | The O&M Contractor is able to analyse and repair faults by means of internal resources (own staff) or external resources (subcontractors, if applicable) in an efficient manner in order to minimise losses. Each corrective maintenance activity includes the following steps: (i) Fault diagnosis (troubleshooting), (ii), Repair and temporary repairs, (iii) Root-cause analysis, (iv) and Documentation and follow up activities | - Sample report including losses due to faults | 1 | 0%
E.5 | Water usage and management | 2 |  |  |  | 0 | The O&M contractor is able to use water judiciously keeping in view the water table and other uses of water in the power plant site, also relying on water-efficient module cleaning solutions. | -Sample report on usage of water for maintenance activities -Description of water-efficient or waterless module cleaning solutions used | 1 | 0%
E.6 | Extraordinary maintenance | 3 |  |  |  | 0 | The O&M Contractor is able to analyse and repair damages due to extraordinary events by means of internal resources (own staff) or external resources (subcontractors, if applicable) in an efficient manner in order to minimise losses. Includes the following steps: (i) Fault diagnosis (troubleshooting), (ii), Repair and temporary repairs, (iii) Root-cause analysis, (iv) and Documentation and follow up activities | - Sample report about extraordinary maintenance activities | 1 | 0%
E.7 | Additional services | 2 |  |  |  | 0 | The O&M Contractor is able to provide all the additional services as listed in the respective section of the O&M Best Practice Guidelines by means of internal resources (own staff) or external resources (subcontractors, if applicable) in an efficient manner, including innovative inspections such as infrared thermography (with drones), I-V curve tracing, electroluminescence imaging and soiling measurements as described in section "10.10. Data collected by specialised PV module field inspections", solutions described in "13.2. Retrofit coatings for PV modules", and Predictive Maintenance analysis. | - Sample report about execution of each of the additional services | 1 | 0%
F | Revamping and repowering | 4 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0 |  |  | 2 | 50%
F.1 | Technical module and inverter repowering | 2 |  |  |  | 0 | The O&M Contractor has the technical ability to plan and execute the replacement of modules and inverters in line with the minimum requirements and best practices decribed in sections "8.2. Module repowering" and "8.3. Inverter repowering". | - Samples/extracts of revamping projects fully executed | 1 | 0%
F.2 | Project implementation capability | 2 |  |  |  | 0 | The O&M Contractor has the technical organization and the commercial ability to implement the revamping/repowering project, including performance analysis, potential assessment, solution design, implementation and review, as described in the section "8.4. General Repowering Considerations". | - Sample performance analysis, potenatial assessment, solution design and review | 1 | 0%
G | Spare Parts Management | 7 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
G.1 | Proper strategy for spare parts management | 3 |  |  |  | 0 | The O&M Contractor has a strategy based on warehousing/storage or agreements with equipment suppliers and/or distributors to optimise the activities related to spare parts management. The stocking level is monitored and following indicators documented: (i) frequency of failure, (ii) impact of failure, (iii) cost of spare part, (iv) degradation over time. | - Evidence of the optimisation strategy, such as cost-benefit analysis, warehouse documentation, or agreements with OEM or distributors | 1 | 0%
G.2 | Spare part register | 2 |  |  |  | 0 | The O&M Contractor has a spare part register that compares the current state with the required stocking level and keeps additional useful information (such as serial numbers). The O&M Contractor has an historical analysis showing who used which spare when. | - Spare part register or other files/table with list of spare parts | 1 | 0%
G.3 | Appropriate spare parts storage and insurance | 2 |  |  |  | 0 | The O&M Contractor secures spare parts against environmental conditions (e.g. humidity or high temperatures) and theft. The O&M Contractor ensures manufacturer's recommendations are followed, e.g., "the stacked modules, in any case, are only stacked as per the manufacturer’s recommendation" . The O&M Contractor insures the spare parts appropriately (if applicable - if spare parts are not insured by the O&M Contractor, they must be insured by the asset owner). | - Documentation of the warehouse (normally necessary for insurance) - Copy of insurance policy | 1 | 0%
H | Data and monitoring requirements | 11 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
H.1 | Monitoring system selection | 3 |  |  |  | 0 | The O&M Contractor should have a clear strategy on its monitoring software. It can use its own system or a third party system or a mix of the two. Plant specific KPIs are normalised with units following the norm 61724 - Chapter 3. The system provides uniform granularity for all the different data collected. Reference is the list of requirements in section "10.2. Monitoring (web) portal" (pages 66-67) of the O&M Best Practices Guidelines. | - Monitoring system documentation such as manual and indicators list with available granularities. | 1 | 0%
H.2 | Configurable alarm management | 3 |  |  |  | 0 | The O&M Contractor makes use of a monitoring system allowing various alarms to be sent by email. All alarms are configurable by the O&M Contractor based on the knowledge of the solar asset. Reference is the list of requirements in section "10.9.8. Alarms" (page 75) of the Best Practices Guidelines. | - Monitoring system documentation with list of available alarms and notification functionality description and description of alarms mangement procedures | 1 | 0%
H.3 | Dataloggers | 2 |  |  |  | 0 | The data loggers selected or recommended by the O&M Contractor can store at least one month of data. Historical data is backed up constantly by sending it to external servers and, after every communication failure, the data logger automatically sends all pending information. Raw real time data and aggregated data are available for the entire lifetime of the project. There is a logbook to track configuration changes. The entire monitoring installation is protected by an uninterruptable power supply (UPS). The O&M Contractor takes the necessary actions to preseve the UPS system. | - Spec sheets and manuals for the mostly used Dataloggers, including, where available, list of indicators and alarms provided - Maintenance record book - Diagram and description of UPS system | 1 | 0%
H.4 | Sensors on site | 1 |  |  |  | 0 | The O&M Contractor is able recommend the installation on site of all necessary sensors needed for a good performance analysis: - at least one solar irradiance measurement devices, ideally pyranometers, for each module orientation plane - at least one ambient temperature per plant - at least onemodule temperature sensors Every sensor should provide data with granularity max 15 minutes. The O&M Contractor maintains the hardware on site clean and well calibrated. The O&M contractor ensures that the available sensors are properly assigned to the different arrays for the calculation of the Performance Ratio (PR) and expected yield. | - Layout sheet of the mostly used sensors as configured in the monitoring system - Description of irradiation reference for Performance Ratio (PR) calculation | 1 | 0%
H.5 | External independent meteo data & forecast references | 1 |  |  |  | 0 | For plants >10 MWp, automated data collection of independent hourly meteo data (ambient temperature, wind speed, snow coverage) is provided through the monitoring interface or from an independent meteo source. When satellite-based irradiance data is used, hourly granularity or less (15 minutes if possible) is used, with data retrieved once per day at least. The O&M Contractor is able to integrate a good solar irradiance and power forecast. | - Description of independent irradiation and meteo services provider (external service or included in the monitoring tool) - Description of irradiation forecast provider and forecast expected yield model (if applicable) | 1 | 0%
H.6 | Cyber security analysis | 1 |  |  |  | 0 | A cyber security analysis is undertaken by the O&M Contractor, starting from a risk assessment (including analysis at the level of the system architecture). The O&M Contractor recommends to the asset owner the implementation of a cybersecurity management system (CSMS) that incorporates a plan-do-check-act cycle. Security of the data is ensured by frequent backups and using encryption and secure protocols. A detailed backup plan is available. Sufficient cybersecurity is ensured according to, e.g, ISO/IEC 27032:2012. | - Description of cybersecurity analysis and suggested CSMS scheme | 1 | 0%
I | Key Performance Indicators (KPIs) | 10 | Fully fulfilled | Partly fulfilled | Not fulfilled | 0
I.1 | Ability to manage and be measured by the Availabilty and Response Time Availability KPIs | 4 |  |  |  | 0 | The O&M Contractor has the ability to manage O&M Contractor KPIs such as Response Time (see 11.3. O&M Contractor KPIs of the O&M Guidelines India edition) and to fulfill at least 99% Contractual Availability (in case of on-site staff) when contractually agreed and where a clear calculation formula is provided in the contract. | - Sample anonymised monthly reporting confirming the fulfilment of the contractual availability including the assessment of Unavailability at least at String or at Inverter level in order to verify the ability to track correctly all the event at component level. - Sample anonymized O&M agreement section defining KPI calculatation/formula | 1 | 0%
I.2 | Ability to calculate and analyse PV Power Plant KPIs | 3 |  |  |  | 0 | The O&M Contractor has the ability to calculate and analyse PV Power Plant KPIs such as Performance Ratio (PR) and Specific Yield, and to use the information to improve its performance. Reference is the list of PV Power Plant KPIs in section 11.2. PV power plant KPIs of the O&M Best Practices Guidelines India edition. For the Indian context, the O&M Contract should be able to calculate the Capacity Utilisation Factor (CUF) also (see section 11.2.5. of the Guidelines India edition). All KPIs included in the O&M contract are included with calculation methodology and formula. | - Monthly reporting template including all PV Power Plant KPIs used by the O&M Contractor | 1 | 0%
I.3 | Proper use of exclusion factors | 2 |  |  |  | 0 | In the calculation of O&M Contractor KPIs and PV Power Plant KPIs used for reporting purposes (such as Availability and PR), the O&M Contractor excludes periods during which the power generation of the plant was reduced due to external (exclusion) factors. In the case of Availability used for contractual purposes, any failure time only begins to run when the O&M Contractor receives the error message. If the data connection to the site was not available, failure time begins after reestablishment of the link. The O&M contract shall also clearly define the exclusion events e.g., Force Majeure. | - Monthly reporting template including the assessment of Unavailability at least at String or at Inverter level in order to verify the ability to track correctly all the event at components' level - Example of O&M agreement section defining exclusion factors | 1 | 0%
I.4 | Proper definition of the Minimum Irradiance Threshold (MIT) | 1 |  |  |  | 0 | The Minimum Irradiance Threshold (MIT) is defined according to site and plant characteristics (e.g. type of inverter, DC/AC ratio etc.). Typical MIT Values are 50 or 70 W/m2. | - Proof of this capability (email, report etc.) - Example of O&M agreement section defining MIT | 1 | 0%